PART 1 - GENERAL

1.1	Work of this section includes:

.1	Provide roof penetration flashing, miscellaneous sheet metal trim,

pitch pockets, and flashing as indicated on the drawings.

1.2	Submittals

.1	Submit manufacturer's product data, installation instructions and

general recommendations for each specified sheet metal and fabricated product.

.2	Submit shop drawings of fabricated sheet metal assemblies indicating

shapes, materials, thicknesses, fastening methods, and relation of adjacent construction.  Field verify existing dimensions and conditions prior to commencement of shop drawings to the greatest extent possible.

PART 2 - PRODUCTS

2.1	Materials, General

.1	Copper:  ASTM B 370; cold rolled except where soft temper is

required for forming; 16 oz, (0.0216" thick) except as otherwise indicated.   Provide lead coating of 0.06 lbs. per sq.ft. on exposed copper surfaces.

.2	Stainless Steel:  AISI Type 304, ASTM A 167, 2D annealed finish,

hard temper as required for forming or performance; 0.027" thick (23 gage), except as otherwise indicated.

.3	Aluminum:  ASTM B 209, alloy 3004, baked siliconized polyester

finish, temper H14, 0.032" thick (20 gage), except as otherwise indicated.

2.2	Roof Penetrations

.1	Single Pipe Penetrations - Fabricate penetration sleeves with 12" high

stack or less, 1" diameter larger than penetrating element and 4" flange at base of flashing turned down 1½" minimum into pipe.  Material shall be 16 oz. copper with lead casting of 0.06 lbs. per sq.ft. of exposed surface except as otherwise indicated.

.2	Provide cap flashing with a draw band of compatible material and

sufficient gauge for pipe penetrations higher than 12" and as indicated on drawings.  Sealants shall be "Dymeric" by Tremco, aluminum color.

.3	Provide roofing manufacturer's standard.

2.3	Pitch Pocket

.1	Provide pitch pockets as required.  Wall or pitch pockets shall be 18

ga. minimum stainless steel with 4" flange at base and turn down 1" at top of pan.  Pitch shall be asphaltic cement with 1" sealer for BUR application or pourable filler compatible with the single ply roof manufacturer.  Set flange on blocking and fabricate pitch pocket to prevent pitch from entering building; provide 2" of non-shrink grout or filler at bottom of pan.

2.4	Miscellaneous

.1	General Metal Fabrications - Shop fabricate to the greatest extent

possible.  Comply with details shown and applicable requirements of SMACNA "Architectural Sheet Metal Manual" and other recognized industry practices.  Form exposed sheet metal without excessive oil-canning, buckling and tool marks, true to line and level with exposed edges folded back to form hems.

.2	Provide for separation of metal from non-compatible metal or

corrosive substrates by coating concealed surfaces at location of contact, with bituminous coating or other permanent separation as recommended by manufacturer/fabricator.

.3	Provide accessories, fastening devices, compression clamps, etc. as

recommended by manufacturer to complete installation of products specified.

PART 3 - EXECUTION

3.1	Installation

.1	Except as otherwise indicated, comply with manufacturer's

installation instructions and recommendations and with SMACNA  'Architectural Sheet Metal Manual".  Anchor units of work securely in place by methods indicated, providing for thermal expansion of metal units; conceal fasteners where possible and set units true to line and level as indicated.  Install work with laps, joints, flanges and seams which will be permanently watertight and weatherproof.

.2	Underlayment - Where stainless steel or aluminum is to be installed

directly on cementitious or wood substrates, install a slip sheet or red rosin paper and a course of polyethylene underlayment.

.3	Install reglets to receive counter-flashing in manner and by methods

indicated.  Fasten reglet wall with ¼" x 1¼" Rawl Zamac Nailins at 12" o.c.

.4	Install gravel stop in compliance with manufacturer's

recommendations.  Install water dam cant prior to laying roofing.  Lap ends ½" and nail with 1" roofing nails at 12" on center roofside and at 24" on center at face side.  Do not nail through lap.  Roofing plies to extend to top of cant.  Cut off flush with front face.  Install fascia after all roofing has been complete.  Slide cover plate in place.  Engage edge.  Lap compression clamp 1".  Check to insure that clamp and fascia are in complete contact.  Punch starter holes in water dam using holes in compression clamp as guide.  Screw clamp tightly to roofing.

.5	Bed flanges of work in a thick coat of bituminous roofing cement

where required for waterproof performance.

3.2	Cleaning and Protection

.1	Clean exposed metal surfaces, removing substances which might

cause corrosion of metal or deterioration of finishes.

.2	Touch-up shop finishes with compatible paint of same color as

required to prevent corrosion.

END OF SECTION