PART 1 - GENERAL

1.1	Work of this section includes:

.1	Provide roof top fire vent at opening indicated on drawings.

.2	Provide roof scuttles indicated on drawings.

1.2	Quality Assurance

.1	Provide fire vent which has been tested, listed and labeled as

follows:

.1	UL listed

.2	FM approved

1.3	Submittals

.1	Submit manufacturer's product data and shop drawings for

fabrication and installation of fire vent.

.2	Submit shop drawings indicating details for conditions at openings,

location and installation requirements.

PART 2 - PRODUCTS

2.1	Approved Manufacturers

.1	Fire vent shall be product equivalent to those specified and

manufactured by the following:

.1	Bilco Company - Type SV

.2	Babcock Davis - Model No. 6-104

.2	Roof scuttles shall be products equivalent to those specified and

manufactured by the following:

.1	Bilco Company- Type S

.2	O'Keeffe's Inc. - RH SS14303615

2.2	Materials

.1	Fire vent and scuttles shall be 30" x 36" single leaf constructed of 14

gauge stainless steel covers with 12" high 14 gauge stainless steel insulated curb.

.2	Fire vent shall include 160° fusible link connected in series with an

electrol thermo link which will hold closed under constant 110 voltage, but will open when there is a break in voltage.  Electrician will provide and connect detectors to thermo link.

.3	Curb shall be 12" in height and of 11 gauge aluminum.  It shall be

formed with a 3½" flange with holes provided for securing to roof deck.  Curb shall be equipped with integral metal cap flashing of same gauge and material as curb, full welded at the corners for absolute weather tightness.  Insulation on the exterior of the curb shall be rigid fiberboard 1" thick.

.4	Units shall be completely assembled with heavy pintle hinges and

compression spring operators enclosed in telescopic tube.

PART 3 - EXECUTION

3.1	Installation

.1	Units shall be installed in accordance with manufacturer's instructions

and recommendations.  Coordinate work with other trades including roofing and electrical.

END OF SECTION