DIVISION 23 - MECHANICAL (HVAC)

GENERAL:

- Review Division 22/23/26/27/28 General Design Requirements.

- Central air handling systems are preferred over unit ventilator systems and should be used on all new or major addition projects.  When economically feasible, major HVAC renovations shall convert to central AHU systems.

- Hot water boiler systems shall be used with central air handlers and finned radiation for improved control.

- Steam boilers shall be used with unit ventilator systems to minimize freeze-up.

- All equipment shall be located in an accessible location.  Rooftop air handling units shall be avoided.

- See division 26 for information on Variable Frequency Drives

SECTION 230513 - MOTORS

- Motors built for 60 Hz. operation, three phase for 1/2 HP and larger, single phase for 1/3 HP and smaller.

- Comply with NEMA standards.

- Bearings rated 20,000 life hours.

- Motors rated 1 HP and larger shall be special design, high efficiency energy saver type with a guaranteed NEMA nominal full-load efficiency by IEEE Standard 112 Test Method B.  Minimum efficiency to meet or exceed NYSERDA rebate requirements.

SECTION 230514 - ELECTRIC WIRING

- Provide wiring in accordance with requirements specified in Division 16 - Electric and the National Electrical Code.

- Low voltage wiring for DDC systems shall be plenum rated cable:

  - Run in bridle rings when above accessible type ceilings.

  - Run in bridle rings at mechanical room ceilings and in crawl spaces.

  - Concealed in occupied spaces where possible or run in [EMT conduit] or [Wiremold] when exposed in occupied spaces or in mechanical rooms from panel or device up to ceiling.

  - All cases not specified shall be in conduit.

SECTION 230519 - GAUGES AND THERMOMETERS

- Water Pressure Gauges:

  - 4-1/2" diameter face.

  - Accuracy - 1% of scale range.

  - Bronze pulsation damper.

  - Provide on pumps, AHU coils, make-up water, heat exchangers, chillers, cooling tower.

- Piping System Thermometers:

  - Bimetal dial.

  - Where maximum temperature is less than 120oF - graduations of 1oF, accurate to within 1/2oF.

  - Where maximum temperature is greater than 120oF - graduations of 2oF, accurate to within 1oF.

  - Provide on boilers, AHU coils, heat exchangers, chillers, cooling towers, steam boiler make-up water.

- Steam Pressure Gauges:

  - 4" diameter face.

  - Range shall be double normal operating pressure.

  - Provide on boilers, main steam header, AHU coils.

- Pressure/Temperature Test Plugs:

  - 1/4" NPT plug with test kit.

  - Sisco "P/T Plugs".

  - Provide on duct mounted reheat coil

SECTION 230523 - VALVES

- Gate Valves (Steam/Condensate Service):

  - 2-1/2" and Larger:  Milwaukee #F-2885A.  OS&Y flanged.  IBBM.

  - 2" and Smaller:  Milwaukee #1152, bronze, solid wedge disc, rising stem, union bonnet.  Screwed or solder ends.

- Globe Valves (Throttling Applications for Steam/Water Service):

  - 2-1/2" and Larger:  IBBT, OS&Y flanged.

  - 2" and Smaller:  Bronze, screwed ends.

- Check Valves:

  - 2-1/2" and Larger:  IBBT, bolted flanged cap, flanged ends.

  - 2" and Smaller:  Bronze, swing check with soldered or screwed ends.

  - Silent Check Valve:  Conbraco "61-500 Series".  Always use with condensate or boiler feed pumps.

- Ball Valves (Chilled Water, Hot Water and Low Pressure Condensate Systems, 2-1/2" and Under):

  - Bronze body with type 316 shaft and ball, full porting and adjustable packing gland.

  - Watts "B6000SS".

- Butterfly Valves (Chilled Water, Hot Water, Condenser Water 3" and over):

  - High performance lug style, type 316 stainless steel disc.

  - 100% bi-directional shutoff at 285 psi.

  - Water Service:  Watts - QF.

- Gas Valves:

  - 2-1/2" and Larger:  Nordstrom "Fig. #143".

  - 2" and Smaller:  Watts - FBV.

- Hose Thread Drain Valves:

  - 1/2" Ball Valve - Watts "B6000CC".

  - Provide with cap and chain.

- Liquid or Vacuum Relief Valves:

  - Lunkenheimer "#658".

- Expansion Compensation:

  - Hot water, chilled water, condenser water systems:  Field piped expansion loops or "Metra-Flex" joints.

  - Steam:  Field piped expansion loops.

  - Bellows type or mechanical joints on pipe systems are not acceptable except if required in finned radiation covers due to space limitations.

- General:  All valves shall be concealed and accessible in classrooms.  Locate valves within cabinetry or enclosures.

SECTION 23200001 - SELF-CONTAINED CONTROL VALVES

- High capacity for steam, Cv=4.6 for 1/2" size.  Medium capacity for water, Cv=2.5 for 1/2" size.  Brass body with replaceable cartridge.  Cartridge replaceable inline, under pressure.

- Valve mounted control unit with remote mounted sensor equipment.

- Honeywell Braukmann #V110 with T10A sensor for steam.  Honeywell Braukmann #V100 with T100 sensor for hot water.

SECTION 230553 - MECHANICAL IDENTIFICATION

- Piping Identification:  Snap on, pressure sensitive or stencil paint type.  Comply with ANSI A13.1.

- Directional flow arrows on all piping.

- Lettering size as follows:

O.D. Pipe				Letter Height

- 3/4" - 1-1/4"				1/2"

1-1/2" - 2"				3/4"

2-1/2" and Over				1"

- Label piping as follows:

Function				Identification

0-15 psi Steam				L.P. Steam

Condensate Return			Cond.

- Hot Water Heating Supply		H.W. Supply

Hot Water Heating Return		H.W. Return

Chilled Water Supply			C.W. Supply

Chilled Water Return			C.W. Return

Condenser Water Return		Cond. W.S.

Condenser Water Supply		Cond. W.R.

*NOTE:  If glycol solution is used, add a "G" to identification.

- Valve Tags:  Seton Style 300.

  - Provide valve tags and charts for all valves 1" and larger.

- Equipment Nameplates:  Seton #2060-20.

  - Provide plastic engraved nameplates on all central equipment.  Labels shall match DDC system Nomenclature where applicable.

- Above ceiling equipment locator stickers:

  - ¾” diameter colored stickers placed on ceiling grid.

  - Fire/smoke dampers – RED

  - Plumbing valves – BLUE

  - VAV Boxes or reheat coils – GREEN

  - HVAC Valves – ORANGE

  - Fans – YELLOW

  - Pumps - BLACK

SECTION 230593- ADJUSTING AND BALANCING

- The Balancing Subcontractor shall be certified by and shall follow procedures and methods published by AABC or NEBB.

- Test, adjust and record the following air side data:

  - Fan Motors:  RPM, BHP, FLA, sheave sizes, shaft diameter, number and size of belt, nameplate data.

  - Fan:  CFM, RPM, suction static pressure, discharge static pressure, sheave sizes, shaft data, nameplate data.

  - Air Handling Units in Minimum O.A. and Economizer Mode:  Outdoor air cfm, discharge cfm, return cfm, static profile through unit, nameplate data.

  - Unit ventilators:  Minimum outside air and total cfm.

  - Coils:  Entering air temperature (WB/DB), leaving air temperature (WB/DB), static differential, face velocity, cfm, nameplate data.

  - VAV Boxes:  Minimum cfm, maximum cfm.

  - Registers, Grilles and Diffusers:  cfm.

- Test, adjust and record the following water side data:

  - Coils:  GPM, EWT, LWT, pressure drop, nameplate data.

  - Pumps:  GPM, suction pressure, discharge pressure, amps, motor rpm, nameplate data.

  - Boilers:  GPM, EWT, LWT, nameplate data.

SECTION 230713 - INSULATION

- Flame spread rating of 25 or less and a smoke develop rating of 50 or less.

- Comply with New York State Energy Conservation Construction Code.

- Piping Systems:

  - Material and thickness as follows:

Insulating			Pipe		Insulation

- Piping System		Material			Size		Thickness

- Hot Water	Glass fiber	>2"	1-1/2"

(2000F and below)	<1-1/2"	1”

- Chilled water	Glass fiber	>2"	1"

- (40-550F)		<1-1/2”	3/4”

- Refrigeration	Glass fiber	>2”	1"

<1-1/2"	. 3/4"

- Low Pressure Steam	Glass fiber	>2"	2"

and condensate	<1-1/2”	1-1/2”

  - Low pressure steam, condensate, hot water or chilled water in high abuse or exposed in areas accessible to students shall be insulated on straight sections with calcium silicate up to 8'-0" AFF.  Elbows and fittings shall be preformed rigid fiberglass.  Cover both fiberglass fittings and calcium silicate with a .030" thick PVC jacket.  Calcium silicate insulation thickness shall be same as above.

  - Rigid Glass Fiber Pipe Insulation:  4 Lbs./Ft.3, .25 Btu-In./Ft.2 Hr. at 75oF maximum.

  - Calcium Silicate Pipe Insulation:  14.5 Lbs./Ft.3, .42 Btu-In./Ft.2 Hr. at 200oF maximum.

- Duct Insulation:

  - Minimum of R-5 when located in unconditioned space.

  - Service, material and thickness as follows:

Service				Material			Thickness

- Air conditioning supply	Exposed:  Rigid	1-1/2"

and heating supply		fiberglass

Concealed: Flexible	2”

fiberglass

- Air conditioning return						....NOT INSULATED....

- Ventilation							....NOT INSULATED....

- Outside air ducts and	Rigid fiberglass	2"

Plenums

Exhaust, relief or vent 	Exposed:  Rigid………………..	1-1/2"                                       ducts and plenums 	fiberglass

(1st 15 ft. from exterior 		Concealed:  Flexible……………1-1/2"                                      opening and plenums)		fiberglass

SECTION 230900- CONTROL SYSTEM

- General:

  - RCSD has a School Board resolution stating that all temperature controls to be Andover Controls provided by Day Automation, Victor, New York.

  - The Control Contractor shall provide a sheet at the start of each project notifying the Custodian and RCSD Inspector who is the Control Installer, Start-up Engineer and back-up person with a day phone number, pager number and emergency number.

  - Installation of the RTC phone line for the DDC system will be specified as part of the Control Subcontractor's responsibility.  Rochester City School District will pay the monthly charges and submit an authorization letter to allow for line installation.  Phone line shall be a dedicated line, not connected to switch.

  - The Engineer shall specify training sessions at start up and after six months for the Custodian. The training scope shall describe what should be covered and will include an overall description of the HVAC system operating and a hands-on trouble shooting session.  Training sessions to last a maximum of four (4) hours.  Control Contractor to submit a training schedule and notify RCSD Plant Maintenance.

  - The Control Contractor shall hold one general DDC system orientation session at their facility for all school custodians receiving DDC controls that year.  The session will be held in the summer and assist the schools in an overall understanding of the systems and servicing of the equipment.  Session shall last eight hours.  Control Contractor shall submit schedule and notify RCSD Plant Engineering.

  - In general, the priorities for project completion shall be installation of controls on new HVAC systems first and conversion of existing pneumatic control to DDC second.  The Rochester City School District Design Group will try to bid DDC to pneumatic conversion projects earlier so this work can take place in the spring and early summer when control work on new HVAC systems is waiting on the Mechanical Contractor.

  - The Control Contractors Start-up Engineer shall be responsible for communicating status of activities and scheduling control work with the Custodian, Principal and Inspector.

  - Pneumatic control devices with a microprocessor based direct digital control system.  See the attached generic points list.

  - All existing pneumatic tubing shall be pressure tested prior to connection to a new device.  Engineer shall include replacement of air mains air compressor and filter dryer on large renovation projects or after major abatement projects.

  - Dampers:  Low leak type.  Normally open return air dampers.  Normally closed outside air, relief air and exhaust air dampers.

  - Personal Computer Workstation:  Computers shall be locked or secured in place.  Computers shall only be used for an interface to the energy management system.

  - Consulting Engineer shall perform a thorough punchlist inspection of the project including verification of system interface to the head-end computers at central office and plant maintenance.  Engineers shall enforce their specification.

  - All alarms shall call out to the head-end computers at central office and plant maintenance.  Alarms shall be received and documented through the printer.

  - All DDC systems shall be interfaced to the head-end computers at central office and plant maintenance.  All graphics available at the school's head-end computer shall be available at the remote head-end computers.

  - On large DDC projects, temperature controls shall be bid as a prime contract.  Review with Design Group.

  - All temperature controls shall be installed by the Temperature Control Contractor including all pneumatic tubing and devices.

  - All contract documents shall include a DDC points schedule.

  - Engineer shall review each project situation to determine if electronic systems would be acceptable and review with Design Group.

  - Electrically operated control valves:

    - Manual override

    - Spring return

    - Siemens Series, Belimo "AF" Series actuators

  - Electric damper operators:

    - Spring return

    - Visual position indicator

    - Belimo "AF" Series

  - All pumps and fans shall have a confirmed status digital input point.

  - All variable speed drives shall have a bypass status digital input point.

  - Heating coil valves shall be normally open.  Cooling coil valves shall be normally closed.

  - The DDC system shall not interrupt the ventilation system operation during occupied hours, except under energy saving scheduling functions.

  - Day Automation shall obtain building occupancy schedule from school district.

- Sequence of Control Operation:

  - Related Documents

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - Summary

    - This Section includes control sequences for HVAC systems, subsystems, and equipment.

    - Related Sections include the following:

      - Division 15 Section "HVAC Instrumentation and Controls" for control equipment and devices and submittal requirements.

    - All sequences of operations contained in this section will meet ASHRAE 62 ventilation requirements. In occupied classrooms 15 CFM of outside air per occupant will be maintained at all times.

    - All ventilation fan shall be operating during occupied times.

  - Definitions

    - DDC:  Direct-digital controls.

    - EMS:  Energy Management System or BAS:  Building Automation System

    - VAV:  Variable air volume.

  - DDC Unit Ventilator With New Occupancy Sensor (Sequence Of Operations #1)

    - General Information

      - The unit contains mixing dampers consisting of two, reciprocally acting blades, which are normally open to return air, and normally closed to outside air. One pneumatic actuator controls the dampers.

      - The supply fan is wired normally open at the control relay and fails off.

      - The unit contains one hot water or steam coil. The unit's capacity is controlled by a hot or steam water valve or a face and bypass damper.

      - Control cycle to follow ASHRAE Cycle II Standard.

    - Safety Interlocks

      - The supply fan shall be commanded off upon activation of any of the following software safeties:

        - System failure alarm trips.

        - Loss of power to the unit.

      - The pneumatic signal to the mixing damper actuator passes through the normally closed port of an EP wired in parallel with the supply fan motor; preventing the mixing dampers from opening when the supply fan is off.

      - If the mixed air temperature falls below 45ºF, provide a general alarm at the building operators workstation. If the mixed air temperature falls below 40ºF, provide a critical alarm at the districts plant maintenance wok station. At no time during the occupied mode shall the outside air damper close.

    - Alarms

      - Supply fan fails to run after 30 seconds of being commanded on.

      - Supply fan fails to stop after 30 seconds of being commanded off.

      - Space temperature is more than 5º below heating setpoint for greater than 5 minutes.

      - Space temperature is more than 5º above cooling setpoint for greater than 5 minutes.

      - Software safety trip.

      - Software safety lockout (4 safety trips in 3 hours).

      - Mixed air temperature below 45º when unit is unoccupied.

    - Common Mode Control

      - Occupied heating setpoint, unoccupied heating set-point, unoccupied cooling set-point, and purge enable/disable shall be global and fully adjustable from any interface.

      - Each unit will have an occupied heating set-point bias that will be capped at +/-4º. Each unit will have an occupied heating/cooling set-point dead band that will be capped at 2º and 10º. Both bias and dead band will be adjustable from any interface.

      - Each unit will have a stagger start number that will keep too many units from starting at the same time, in effect, flattening load peaks.

      - Each unit will have a software HOA for control of the supply fan.

    - Unoccupied Mode Control

      - The supply fan shall be turned off.

      - If the space temperature drops 1ºF below the unoccupied heating setpoint, the supply fan shall be commanded on, the mixing dampers shall remain closed, and the heating valve shall modulate open. When the space temperature rises 1ºF above the unoccupied heating setpoint, the supply fan shall be commanded off.

      - If the mixed air temperature drops below 45º the supply fan shall be commanded on and the heating valve shall go to full open for the remainder of the unoccupied period and an alarm will be generated at the operator interface.

    - Unoccupied Mode Control From Occupancy Sensor

      - During the scheduled occupied mode, when the space is unoccupied as sensed by the room occupancy sensor, the damper will be closed to outside air.

      - The space temperature set-point shall be reset to 2ºF (adj.) lower than the occupied set-point.

      - The supply fan will cycle on and off to maintain the space temperature set-point. If the space temperature drops 1º below the reset heating set-point, the supply fan shall be commanded on, the mixing damper shall remain closed, and the heating valve shall modulate open. When the space temperature rises 1º above the reset heating setpoint, the supply fan shall be commanded off.

      - If the mixed air temperature drops below 45º the supply fan shall be commanded on and heating valve shall remain open for the remainder of this period and an alarm will be generated at the operators interface.

      - When the space is occupied as sensed by the room occupancy sensor, the sequence will be indexed to the occupied mode.

    - Purge Mode Control

      - Purge mode (fresh air changeover) shall only be permitted during an unoccupied period.

      - If the outside air is between 45º and 60º and the space temperature rises above 75º, the supply fan shall be commanded on, the mixing dampers shall be fully open, and the heating coil shall be fully closed. When the space temperature drops to 70º, the supply fan shall be commanded off and the mixing dampers shall return to the normal position.

    - Warm-Up Mode Control

      - Optimum start duration shall be determined based on outside air temperature.

      - During the optimum start period, the heating set-point will be linearly ramped up from unoccupied heating set-point to occupied heating set-point.

      - When the heating setpoint crosses above the space temperature, the supply fan will be commanded on, the mixing dampers shall remain closed, and the heating valve will modulate to maintain heating setpoint.

    - Cool-Down Mode Control

      - Optimum start duration shall be determined based on outside air temperature.

      - During the optimum start period, the cooling setpoint will be linearly ramped down from unoccupied cooling setpoint to occupied cooling set-point.

      - When the cooling setpoint crosses below the space temperature, the supply fan will be commanded on, the mixing dampers shall modulate to maintain cooling setpoint.

    - Occupied Mode Control

      - The supply fan will run continuously.

      - The mixing dampers will maintain minimum ventilation requirements.

      - The mixing dampers will modulate when economizer cooling is available to maintain cooling set-point.

      - The heating valve will modulate to maintain heating set-point.

      - The discharge air temperature will be limited to the following low discharge air reset schedule:

Outside Air Temperature		Discharge Air Draft Limit

0º F					65ºF

55º					55º

- This will prevent drafting and cycling of the discharge air temperature.

  - Unit Ventilator To DDC With New Occupancy Sensor (Sequence Of Operations #2)

    - General Information

      - The unit contains mixing dampers consisting of two, reciprocally acting blades, which are normally open to return air, and normally closed to outside air. One pneumatic actuator controls the dampers.

      - The supply fan is wired normally open at the control relay and fails off.

      - The unit contains one hot water coil. The unit's capacity is controlled by a hot water valve.

      - Control cycle to follow ASHRAE Cycle II Standard.

    - Safety Interlocks

      - The supply fan shall be commanded off upon activation of any of the following software safeties:

        - System fire alarm trips.

        - Loss of power to the unit.

      - The pneumatic signal the mixing damper actuator passes through the normally closed port of an EP wired in parallel with the supply fan motor; preventing the mixing dampers from opening when the supply fan is off.

      - If the mixed air temperature falls below 45ºF, provide a general alarm at the building operators workstation. If the mixed air temperature falls below 40ºF, provide a critical alarm at the districts plant maintenance workstation. At no time during the occupied mode shall the outside air damper close.

    - Alarms

      - Supply fan fails to run after 30 seconds of being commanded on.

      - Supply fan fails to stop after 30 seconds of being commanded off.

      - Space temperature is more than 5º below heating setpoint for greater than 5 minutes.

      - Space temperature is more than 5º above cooling setpoint for greater than 5 minutes.

      - Software safety trip.

      - Software safety lockout (4 safety trips in 3 hours).

      - Mixed air temperature below 45º when unit is unoccupied.

    - Common Mode Control

      - Occupied heating setpoint, unoccupied heating set-point, unoccupied cooling set-point, and purge enable/disable shall be global and fully adjustable from any interface.

      - Each unit will have an occupied heating set-point bias that will be capped at +/-4º. Each unit will have an occupied heating/cooling set-point dead band that will be capped at 2º and 10º. Both bias and dead band will be adjustable from any interface.

      - Each unit will have a stagger number that will keep too many units from starting at the same time, in effect, flattening load peaks.

      - Each unit will have a software HOA for control of the supply fan.

    - Unoccupied Mode Control From DDC System

      - The supply fan shall be turned off.

      - If the space temperature drops 1ºF below the unoccupied heating setpoint, the supply fan shall be commanded on, the mixing dampers shall remain closed, and the heating valve shall modulate open. When the space temperature raises 1ºF above the unoccupied heating setpoint, the supply fan shall be commanded off.

      - If the mixed air temperature drops below 45º the supply fan shall be commanded on and the heating valve shall go to full open for the remainder of the unoccupied period and an alarm will be generated at the operator's interface.

    - Unoccupied Mode Control From Occupancy Sensor

      - During the scheduled occupied mode, when the space is unoccupied as sensed by the room occupancy sensor, the damper will be closed to outside air.

      - The space temperature set-point shall be reset to 2ºF (adj.) lower than the occupied set-point.

      - The supply fan will cycle on and off to maintain the space temperature set-point. If the space temperature drops 1ºF below the reset heating set-point, the supply fan shall be commanded on, the mixing damper shall remain closed, and the heating valve shall modulate open. When the space temperature raises 1ºF above the reset heating setpoint, the supply fan shall be commanded off.

      - If the mixed air temperature drops below 45º the supply fan shall be commanded on and heating valve shall remain open for the remainder of this period and an alarm will be generated at the operators interface.

      - When the space is occupied as sensed by the room occupancy sensor, the sequence will be indexed to the occupied mode.

    - Purge Mode Control

      - Purge mode (fresh air changeover) shall only be permitted during an unoccupied period.

      - If the outside air is between 45º and 60º and the space temperature rises above 75º, the supply fan shall be commanded on, the mixing dampers shall be fully open, and the heating coil damper shall be fully closed. When the space temperature drops to 70º, the supply fan shall be commanded off and the mixing dampers shall return to the normal position.

    - Warm-Up Mode Control

      - Optimum start duration shall be determined based on outside air temperature.

      - During the optimum start period, the heating set-point will be linearly ramped up from unoccupied heating set-point to occupied heating set-point.

      - When the heating setpoint crosses above the space temperature, the supply fan will be commanded on, the mixing dampers shall remain closed, and the heating valve will modulate to maintain heating setpoint.

    - Cool-Down Mode Control

      - Optimum start duration shall be determined based on outside air temperature.

      - During the optimum start period, the cooling setpoint will be linearly ramped down from unoccupied cooling setpoint to occupied cooling set-point.

      - When the cooling setpoint crosses below the space temperature, the supply fan will be commanded on, the mixing dampers shall modulate to maintain cooling setpoint.

    - Occupied Mode Control

      - The supply fan will run continuously.

      - The mixing dampers will maintain ventilation requirements.

      - The mixing dampers will modulate when economizer cooling is available to maintain cooling set-point.

      - The heating valve will modulate to maintain heating set-point.

      - The discharge air temperature will be limited to the following low discharge air reset schedule:

- Outside Air Temperature		Discharge Air Draft Limit

- 0º F	65ºF

- 55ºF	55ºF

- This will prevent drafting and cycling of the discharge air temperature.

  - Typical Fan Coil Unit With Occupancy Sensor (Sequence Of Operations #3)

    - Fan Coil Units With Outside Air Only

      - The DDC system seven-day time clock shall provide occupied/unoccupied scheduling of the fan coil units.

      - During occupied mode, the fan shall run continuously. The space sensor will modulate outside and return air dampers, subject to a 55ºF discharge low limit, in sequence with the heating control valve to maintain its setting according to ASHRAE Cycle #2. The discharge high limit temperature setpoint shall be set at 125ºF and generate an alarm to the operator work station. The sensor shall intermittently start and stop the fan and open the heating control valve.

      - Unoccupied Mode Control From Occupancy Sensor

        - During the scheduled occupied mode, when the space is unoccupied as sensed by the room occupancy sensor, the damper will be closed to outside air.

        - The space temperature set-point shall be reset to 2ºF (adj.) lower than the occupied set-point.

        - The supply fan will cycle on and off to maintain the space temperature set-point. If the space temperature drops 1ºF below the reset heating set-point, the supply fan shall be commanded on, the mixing damper shall remain closed, and the hot water valve shall modulate open. When the space temperature rises 1ºF above the reset heating setpoint, the supply fan shall be commanded off.

        - If the mixed air temperature drops below 45º the supply fan shall be commanded on and hot water valve shall remain open for the remainder of this period and an alarm will be generated at the operators interface.

        - When the space is occupied as sensed by the room occupancy sensor, the sequence will be indexed to the occupied mode.

  - Typical Air Handling Unit To DDC (Sequence Of Operations #4)

    - Constant Volume Air Handling Units

      - Air handling unit is a constant volume heating unit. Unit operates in occupied/unoccupied modes as determined by the DDC building time clock system.

      - Occupied Mode:  The time clock shall instruct the supply fan to run continuously. Outside air damper shall open to its minimum position. Units shall operate through dry bulb comparison economizer to provide continuous 65º DB (adjustable) supply air temperature when required. The DDC system shall compare the dry bulb temperature of the outside air with the dry bulb temperature of the return air. If the outside air temperature is less than the return air temperature, the outside air and return air dampers shall modulate to provide 65º supply air temperature. If supply air temperature can not be maintained and become lower than required due to minimum outside air qualities then system shall full modulate the normally open to coil three-way heating coil control valve to provide the supply air temperature required. In addition, the heating coil control valve shall modulate further as necessary to satisfy the space sensor, subject to a high limit of 100ºF discharge air temperature.

      - Unoccupied Mode:  Supply fan shall be shut off. Return air dampers shall be full open and outside air dampers shall be fully closed. The heating coil and fan shall cycle to maintain 60ºF unoccupied space temperature setpoint.

      - Fire Mode:  Upon a fire alarm condition as reported by the fire alarm panel, the air handling unit's supply fan shall be off, heating coil control valve shall be full bypass outside air damper fully closed. If the fire alarm is cancelled, the air-handling unit shall be instructed to return to normal occupied/unoccupied modes.

      - Smoke Detection Within The Air Handling Units:  The air handling unit shall turn off and the outside air damper shall close upon a detection of smoke by a smoke detector located in the supply air duct and provided/installed by the Electrical Contractor.

      - Freezstat Control:  A low temperature sensor mounted downstream and sensing full face of heating coil shall, upon detecting a temperature of 37ºF or less, turn off the supply fan, open the hot water control valve to the heating coil fully. Close the outside air damper fully, and open the return air damper fully. Air handling unit will not be allowed to return to non-freezestat, normal conditions unit alarm is acknowledged by manual reset at the AHU.

  - Typical Air Handling Unit To DDC (Retrofit) (Sequence Of Operations #5)

    - Constant Volume Air Handling Units

      - Air handling unit is a constant volume hot water heating unit. Unit operates in occupied/unoccupied modes as determined by the DDC building time clock system.

      - Occupied Mode:  The time clock shall instruct the supply fan to run continuously. Outside air damper shall open to its minimum position. Units shall operate through dry bulb comparison economizer to provide continuous 65º DB (adjustable) supply air temperature when required. The DDC system shall compare the dry bulb temperature of the outside air with the dry bulb temperature of the return air. If the outside air temperature is less than the return air temperature, the outside air and return air dampers shall modulate to provide 65º supply air temperature. If supply air temperature can not be maintained and become lower than required due to minimum outside air qualities, then system shall full modulate the normally open to coil three-way heating coil control valve to provide the supply air temperature required. In addition, the heating coil control valve shall modulate further as necessary to satisfy the space sensor, subject to a high limit of 100ºF discharge air temperature.

      - Unoccupied Mode:  Supply fan shall be shut off. Return air dampers shall be full open and outside air dampers shall be fully closed. The heating coil and fan shall cycle to maintain 60ºF unoccupied space temperature setpoint.

      - Fire Mode:  Upon a fire alarm condition as reported by the fire panel, the air handling unit's supply fan shall be off, heating coil control valve shall be full bypass, outside air damper fully closed. If the fire alarm is cancelled, the air-handling unit shall be instructed to return to normal occupied/unoccupied modes.

      - Smoke Detection Within The Air Handling Units:  The air handling unit shall turn off and the outside air damper shall close upon a detection of smoke by a smoke detector located in the supply air duct and provided/installed by the Electrical Contractor.

      - Freezestat Control:  A low temperature sensor mounted downstream and sensing full face of heating coil shall, upon detecting a temperature of 37ºF or less, turn off the supply fan, open the hot water control valve to the heating coil fully. Close the outside air damper fully, and open the return air damper fully. Air handling unit will not be allowed to return to non-freezestat, normal conditions unit alarm is acknowledged by manual reset at the AHU.

  - DDC Air Handling Unit With CO² Sensor (Sequence Of Operations #6)

    - Single Zone, Constant Volume Air Handling Units Only (Serving Non-Classroom Areas)

      - Air handling unit is a constant volume hot water heating unit. Unit operates in occupied/unoccupied modes as determined by the DDC building time clock system.

    - Occupied Mode

      - The time clock shall instruct the supply fan to run continuously. Outside air damper shall open to its minimum position. Units shall operate through dry bulb comparison economizer to provide continuous 65° DB (adjustable) supply air temperature when required. The DDC system shall compare the dry bulb temperature of the outside air with the dry bulb temperature of the return air. If the outside air temperature is less than the return air temperature, the outside air and return dampers shall modulate to provide 65º supply air temperature. If the supply air temperature can not be maintained and become lower than required due to minimum outside air quantities, then system shall full modulate the normally open coil three-way heating coil control valve to provide the supply air temperature required. In addition, the heating coil control valve shall modulate further as necessary to satisfy the space sensor, subject to a high limit of 100ºF discharge air temperature.

    - Unoccupied Mode

      - Supply fan shall be shut off. Return air dampers shall be full open and outside air dampers shall be fully closed. The heating coil and fan shall cycle to maintain 60ºF unoccupied space temperature setpoint.

    - Fire Mode

      - Upon a fire alarm condition as reported by the fire alarm panel, the air handling unit’s supply fan shall be off, heating coil control valve shall be full bypass, outside air damper fully closed. If the fire alarm is cancelled, the air handling unit shall be instructed to return to normal occupied/unoccupied modes.

    - Smoke detection within the Air Handling Units

      - The air handling unit shall turn off and the outside air damper shall close upon a detection of smoke by a smoke detector located in the supply air duct and provided/installed by the Electrical Contractor.

    - Freezestat Control

      - A low temperature sensor mounted downstream and sensing full face of heating coil shall upon detecting a temperature of 73ºF or less, turn off the supply fan, open the hot water control valve to the heating coil fully. Close the outside air damper fully, and open the return air damper fully. Air handling unit will not be allowed to return to non-freezestat, normal conditions unit alarm is acknowledged by manual reset at the AHU.

    - Ventilation Control Based CO2 Level in Space

      - During occupied periods, the minimum outside air damper position or fan speed (for 100% OA units) shall be determined based on schedule occupancy through the DDC system. The scheduled occupancy schedules will be user adjustable. A return air CO2 sensor will initiate an alarm back to the DDC system if the measured CO2 level in the space is greater than 900 ppm. If acceptable, exhaust fans or relief dampers will be staged based on the position of the outside air damper. Mixed air low limit and economizer sequences will remain in place. During unoccupied periods, the outside air damper will remain in the closed position.

  - DDC Air Handling Unit With New Occupancy Sensor (Sequence Of Operations #7)

    - Single Zone, Constant Volume Air Handling Units

      - Air handling unit is a constant volume hot water heating unit. Unit operates in occupied/unoccupied modes as determined by the DDC building time clock system.

    - Occupied Mode

      - The time clock shall instruct the supply fan to run continuously. Outside air damper shall open to its minimum position. Units shall operate through dry bulb comparison economizer to provide continuous 65° DB (adjustable) supply air temperature when required. The DDC system shall compare the dry bulb temperature of the outside air with the dry bulb temperature of the return air. If the outside air temperature is less than the return air temperature, the outside air and return dampers shall modulate to provide 65º supply air temperature. If the supply air temperature can not be maintained and become lower than required due to minimum outside air quantities, then system shall full modulate the normally open coil three-way heating coil control valve to provide the supply air temperature required. In addition, the heating coil control valve shall modulate further as necessary to satisfy the space sensor, subject to a high limit of 100ºF discharge air temperature.

      - When the room is unoccupied as sensed by the room occupancy sensor, the outside air damper will be closed or the fan speed will be reduced to 60% (adj.). Minimum ventilation rate will always be supplied to the space when the room is occupied.

      - If applicable, exhaust fans or relief dampers will be staged based on the outside air damper position of the air handling unit.

    - Unoccupied Mode

      - Supply fan shall be shut off. Return air dampers shall be full open and outside air dampers shall be fully closed. The heating coil and fan shall cycle to maintain 60ºF unoccupied space temperature setpoint.

    - Fire Mode

      - Upon a fire alarm condition as reported by the fire alarm panel, the air handling unit’s supply fan shall be off, heating coil control valve shall be full bypass, outside air damper fully closed. If the fire alarm is cancelled, the air-handling unit shall be instructed to return to normal occupied/unoccupied modes.

    - Smoke Detection Within The Air Handling Units

      - The air handling unit shall turn off and the outside air damper shall close upon a detection of smoke by a smoke detector located in the supply air duct and provided/installed by the Electrical Contractor.

    - Freezestat Control

      - A low temperature sensor mounted downstream and sensing full face of heating coil shall, upon detecting a temperature of 37ºF or less, turn off the supply fan, open the hot water control valve to the heating coil fully. Close the outside air damper fully, and open the return air damper fully. Air handling unit will not be allowed to return to non-freezestat, normal conditions unit alarm is acknowledged by manual reset at the AHU.

  - DDC VAV Box Unit With Heating Coil And New Occupancy Sensor (Sequence Of Operations #8)

    - General Information

      - VAV boxes are served from AHU’s.

    - Common Mode Control

      - When the associated air handling unit is in warm-up, the VAV box shall be in the occupied mode.

    - Alarms

      - Space temperature ±5ºF.

    - Warm-up Mode

      - The VAV box damper shall open fully and the reheat control valve shall open to minimum space temperature.

    - Occupied Mode

      - The VAV box damper shall modulate to maintain space temperature.

      - On a drop is space temperature, the VAV box damper shall revert to minimum position and the reheat coil control valve and the room radiation control valve shall modulate as necessary.

    - Unoccupied Mode

      - The VAV box damper shall be at minimum position.

      - The reheat coil and the room radiation control valve shall modulate to maintain unoccupied space temperature of 60ºF.

    - Unoccupied Mode Control From Occupancy Sensor

      - During the occupied period, when the space is unoccupied as sensed by the room occupancy sensor, the damper will be closed to minimum position.

      - The space temperature setpoint shall be reset to plus 2ºF (adj.) during the cooling mode and minus 2°F during the heating mode. The damper will modulate to maintain the reset space temperature setpoint.

      - When the space is occupied as sensed by the room occupancy sensor, the sequence will be indexed to the occupied mode.

  - Radiant Panels/Radiant Heaters/Fin Tube Radiation To DDC (Sequence Of Operations #9)

    - With the DDC system indexed to occupied mode, the space sensor shall call for heating and the heating valve shall modulate or open/close to maintain occupied (adj.) space temperature setpoint.

    - With the DDC system indexed to unoccupied mode, the space sensor shall call for heating and the heating valve shall modulate or open/close to maintain unoccupied (adj.) space temperature.

  - Typical Exhaust Fan Control (Sequence Of Operations #10)

    - Exhaust Fans shall be enabled and disabled accordingly based upon a pre-determined program schedule or interlock, the position of the corresponding outside air damper, and/or the speed of the corresponding supply fan.

    - If a fan is scheduled to operate and status is not validated by the current sensing switch, generate an alarm to all operator interfaces.

    - Fan status shall be monitored for run time accumulation and shall be incorporated into a run time report.

  - Typical Cabinet Unit Heaters And / Unit Heaters (Sequence Of Operations #11)

    - During occupied mode, on a call for heating, the fan shall cycle to maintain 72°F space temperature as sensed by the wall mounted space sensor.

    - With the DDC system indexed to unoccupied mode the fan shall cycle on to maintain 62°F space temperature as sensed by the wall mounted space sensor.

  - Boiler Combustion Controls (Nexus) (Sequence Of Operations #12)

    - Boilers shall be automatically enabled through the DDC temperature control system. Firing rates to be modulated by Nexus controls. DDC system shall determine the lead boiler. If lead Boiler can not maintain steam supply pressure or water temperature, the Nexus system shall enable the lag boiler. The DDC temperature control system shall monitor boiler status through a single contact available on the burner controller provided with each boiler. The DDC temperature control system shall monitor boiler alarm through a single contact available on the burner controller provided with each boiler. If any boiler should incur a flame failure, the boiler system shall be taken off-line and an alarm to the DDC temperature control system shall be generated. A manual acknowledgment of the alarm will be necessary to clear the alarm fault.

    - The sequencing of the lead and lag boiler order shall be adjustable through the DDC system. Each boiler shall be enabled or disabled through DDC system. The default for each boiler will be enabled.

    - Provide a graphic of the boiler status and its lead lag sequence number (ex. 1,2 or 3). The default lead/lag status will be as previously stated.

    - Each combustion air damper shall be interlocked with its respective boiler to open when the boiler fires.

    - Make all required changes on the operator workstation. Make all required changes, including graphic changes at the workstation located at the Central Maintenance Office.

  - Steam To Hot Water Heat Exchanger (Sequence Of Operations #13)

    - The circulation pumps will be setup for lead/lag operation and will be equipped with start/stop function and status monitoring. These pumps shall operate during all occupied hours when the boiler plant is operating.

    - During unoccupied hours, the pumps shall operate whenever the outside air temperature is below 50°F. The pumps shall be off when outside air temperature is about 50°F.

    - The 1/3 and 2/3 low pressure steam control valves shall maintain the loop supply temperature at the linearly interpolated valve based on the relationship of 0°F OA temperature equaling 180°F  HWS temperature and 65°F OA temperature equaling 100°F HWS temperature.

  - Package Rooftop A/C Units With Variable Air Volume Terminal Units (Sequence Of Operations #14)

    - Constant Volume Rooftop Unit

    - On a call for cooling, the supply fan and condensing unit shall be energized and the outside air damper shall open.

    - On a call for heating, the supply fan shall be energized and the outside air damper shall be open. The hot water preheat coil control valve shall modulate to maintain a constant 55°F discharge air setpoint.

    - Rooms with fin tube radiation serving the exterior will be sequenced with the variable air volume terminal unit reheat coil.

    - Occupied Mode:

      - The supply fan shall run continuously.

      - The outside air damper shall open to the minimum setting and the system will modulate between heating and cooling to maintain space temperature setpoint. Whenever the return air enthalpy is greater than the outside air enthalpy, the unit shall be on economizer. The dampers shall modulate in sequence to maintain the discharged air setpoint subject to a mixed air low limit of 50°F. The variable air volume terminal unit shall modulate air volume to maintain 75°F space temperature setpoint. On a drop in space temperature, the variable air volume terminal unit shall modulate to minimum air volume and reheat coil control valve to modulate to maintain space temperature setpoint.

    - Unoccupied Mode

      - The fan and heating coil shall cycle as required to satisfy unoccupied heating setpoint.

      - The cooling system will be disabled.

    - Provide discharge air sensors at all VAV reheat coils.

  - Steam Boilers (Sequence Of Operations #15)

    - The DDC system shall enable and disable the boilers. The building operator shall start/stop the boilers.

    - The boilers will be stage on to maintain steam pressure setpoint.

    - The DDC system shall provide lead/lag control.

    - The DDC system shall monitor boiler status, boiler alarm, steam pressure and condensate temperature.

    - Provide an end switch to prove that the combustion air damper is open before the boilers are allowed to fire.

  - Chilled Water Cooling Plant Control (Sequence Of Operations #16)

    - The chiller system will be allowed to run above 65°F. outside air.

    - Upon a call for the chiller to start the chilled water and condenser water pumps will be started. Upon proof of water flow in both circuits the tower outside air and exhaust air dampers will be opened. Upon proof of damper open via damper end switches, the chiller will be started. The starting of the chiller is to match the occupancy of the building and the mechanical cooling requirements.

    - During the unoccupied mode this system will be off.

    - The chiller will maintain chilled water setpoint via manufacturer supplied controls.

    - The DDC control system will reset the chiller setpoint based on the building load and the building KW demand value. Room setpoints shall follow accordingly.

    - The cooling towers will stage in four (4) steps as needed to maintain the condenser water supply temperature setpoint. First stage – open outside and exhaust air dampers and start tower no.1 pony fan; second stage – start pony fan on tower no. 2; third stage – stop tower no. 1 pony fan; 15 second delay and start primary fan on tower no. 1; fourth stage – stop tower no. 2 pony fan; 15 second delay and start primary fan on tower no. 2. This sequence to be reversed for decreased load.

    - High and low temperature alarms will shut down the chiller and cooling towers.

  - Heating System – Hot Water Boiler (Sequence Of Operations #17)

    - General Information:

      - The boilers and hot water pumps shall be wired N.C.

      - The combustion air dampers limit switch shall be hardwired to boiler circuit and fail N.O.

    - Alarms:

      - System failure

      - Hot water pump failure

      - Boiler failure

      - Boiler water supply setpoint low/high limits

      - Boiler water return setpoint low/high limits

      - Hot water pumps differential pressure sensor low/high limits

      - Hot water supply setpoint low/high limits

      - Hot water return setpoint low/high limits

      - System differential pressure sensors low/high limits

    - Heating Enable/Disable:

      - The occupied period heating enable setpoint shall initially be set for 60°F. (adj.).

        - The unoccupied period heating enable setpoint shall be set at the occupied temperature setpoint minus 10°F.

        - Enable the heating plant when outside air is below the maximum of the heating enable setpoint and 40°F.

        - Disable the heating plant when outside air temperature is 2° above the maximum of the heating enable setpoint and 40°F.

    - Primary Hot Water Pump Control:

      - When the heating plant is enabled the lead pump shall start.

      - If after one minute, proof of flow fails stop the lead pump, start the standby pump and generate an alarm at all operator interfaces.

      - If both pumps fail, start both pumps and generate an alarm at all operator interfaces.

      - Stop both pumps if the heating plant is disabled and both boiler run indicators are off.

    - Boilers:

      - If primary pump flow is proven and the heating plant is enabled, turn on a call for lead boiler.

      - If primary pump flow is not proven, or the heating plant is disabled, turn off a call for lead boiler.

      - When the combustion air dampers are 100% open, and the call for lead boiler is on, the lead boiler will start.

      - If the call for lead boiler is off, or damper position is less than 100% open, the lead boiler will stop.

      - If lead boiler run indication is not seen after 2 minutes, stop the lead boiler, start the lag boiler and generate an alarm at all operator interfaces.

      - If the hot water supply temperature setpoint cannot be maintained by the lead boiler turn on the call for lag boiler.

      - If lag boiler run indication is not seen after 2 minutes, start both boilers and generate an alarm at all operator interfaces.

      - The boiler will cycle on their internal and operating controls.

    - Secondary Reset Loop Hot Water Control:

      - When the heating plant is enabled the lead pump shall start.

      - If after one minute, proof of flow fails stop the lead pump, start the standby pump and generate an alarm at all operator interfaces.

      - If both pumps fail, start both pumps and generate an alarm at all operator interfaces.

      - Stop both pumps if the heating plant is disabled and both boiler run indicators are off.

      - The heating pumps shall operate continuously at variable speed drive as indexed through the variable frequency drives by the hot water differential pressure sensors.

      - The inlet and bypass valves shall modulate to maintain hot water supply setpoint.

      - The hot water supply setpoint shall be reset by the following reset schedule:

- Outside Air Temp 			Hot Water Supply Setpoint

- 60°F					      120°F

- 0°F					      200°F

      - The three-way control valves shall maintain a minimum entering water temperature of 40°F below boiler water setpoint via entering water temperature sensor.

  - Intake/Relief Ventilator Control (Sequence Of Operations #18)

    - General:

      - Intake/relief air damper is normally closed.

    - Occupied Mode: Intake/relief air damper is open.

    - Unoccupied Mode: Intake/relief air damper is closed.

  - Heat Recovery Units (Sequence Of Operations #19)

    - Heat Recovery Unit:

      - The heat recovery unit is controlled by the building EMS with its own application specific controller.

      - During the occupied mode, the unit supply fan and exhaust fan shall run continuously. The automatic outside air and exhaust air dampers at the building penetrations shall open.

      - The 3-way hot water control valve shall modulate to maintain the constant discharge air temperature of 60°F (adj.).

      - During the unoccupied mode, the unit supply fan and exhaust fan shall be off. The outside air and exhaust air dampers at the building penetrations shall close.

      - During morning warm-up and defrost modes, the bypass damper will be open, the outside air and exhaust dampers will be shut, and the preheat and reheat coils will sequence as required to achieve the occupied setpoint.

      - The building EMS shall monitor the entering outside air temperature, leaving exhaust air temperature, return air temperature, heat wheel discharge air temperature and heating coil discharge air temperature.

      - The building EMS shall monitor supply fan and exhaust fan run status.

      - During the economizer mode “free cooling”, the bypass damper will be shut, the outside air and exhaust air dampers will be open and the heat recovery wheel will not rotate.

  - Gas Fired Heaters (Sequence Of Operations #20)

    - During the occupied mode, on a call for heating the fan shall cycle and the gas valve shall modulate to maintain 72°F space temperature, as sensed by the space temperature sensor.

    - During the unoccupied mode, the fan shall cycle on and the gas valve shall modulate to maintain night set back temperature as sensed by the space temperature sensor.

  - VSD Control Of HW Pumps (Sequence Of Operations #21)

    - Each set of pumps shall be operated in a lead/lag sequence to equalize the run time of the two pumps. When enabled, the lead pump shall start. Upon failure of the lead pump, as sensed by a current sensing status switch, an alarm shall be generated, the pump shall be turned off, and the lag pump shall start. Upon a failure of the lag pump, as sensed by a current sensing status switch, an alarm shall be generated; the pump shall be turned off.

    - If the pump set contains variable speed drive, they shall be controlled to maintain a constant static pressure as sensed by a pressure sensor located two-thirds of the way downstream of the pump in the longest or most critical pipe.3

  - AC Units (Sequence Of Operations #22)

    - Units shall be controlled with the unit provided controls and thermostats.

    - Room temperature shall be monitored by the space sensor.

    - The unit shall be enabled during occupied times to maintain temperature setpoint. The unit shall be disabled during unoccupied times.

    - If space temperature drops below defined setpoint, the software shall stop the AC, and print an alarm message at the operator’s terminal indicating room number and space temperature.

  - Zone Control (Sequence Of Operations #23)

    - Hot Deck/Cold Deck Damper Boxes

      - Occupied Mode

        - The space sensor shall monitor the space temperature and modulate the damper to control hot deck/cold deck air entering the room to maintain occupied room setpoint. Upon a call for heating, the damper shall modulate to bring in more air from the hot deck and upon a call for cooling; the damper shall modulate to bring in more air from the cold deck.

      - Unoccupied Mode

        - The space sensor shall monitor the space temperature and modulate the damper to control hot deck/clod deck air entering the room to maintain unoccupied room setpoint. Upon a call for heating, the damper shall modulate to bringing more air from the hot deck and upon a call for cooling; the damper shall modulate to bring in more air from the cold deck.

      - Alarms – Provide an alarm for each of the following:

        - Space Temperature low/high limits. If discharge temperature is below 45°F, the software shall stop the AHU, close outside air damper, and print an alarm message at the operator’s terminal indicating room number and discharge temperature.

  - On-Line Graphics Generation with Dynamic Point Values and Set Points to include:

    - All floor plans shown graphically.

    - All mechanical equipment controlled by the BAS, including all rooms with space temperature sensor, shall be shown graphically.

    - System schematic graphic of the following (each graphic shall include all points related to the system plus the common outside air temperature):

      - Hot water boilers and pumps.

      - Unit ventilators.

      - Ventilation air handling units.

  - Critical Alarm:

    - Alarms are sent out through the district email server as directed by the Owner.

    - Loss of pumps, loss of boilers, low temperature in spaces, high make-up water flow or loss of electrical power.

  - All food service coolers and freezers shall have a high temperature alarm switch.

  - All workstations and building controllers shall be connected to RCSD Wide Area Network (ETHERNET).

  - Acceptable Make:  Andover.

SECTION 232000 - PIPING SYSTEMS AND ACCESSORIES

- Hot Water Heating:  Schedule 40, black steel with screwed, welded or grooved rigid mechanical connections.

- Hot Water Heating (Optional):  Type L copper with soldered connections.

- Hot Water Heating (Optional):  Type L copper with press fit connections.

- Chilled Water:  Schedule 40, black steel with screwed welded, or grooved rigid mechanical  connections.

- Chilled Water (Optional):  Type L copper with soldered connections.

- Refrigerant:  Type L refrigerant grade copper with brazed connections.

- Low Pressure Steam:  Schedule 40, black steel with welded or flanged connections.  Screwed connections are allowed on 2" and smaller and in mechanical rooms.

- Condensate:  Schedule 80, black steel with welded, flanged or screwed fittings.

- Condenser Water:  Schedule 40, black steel with welded, screwed or grooved rigid mechanical connection.

- Flexible Connectors:  3/4" through 2" Size:  Keflex "Model KFCB", 2-1/2" and Larger:  Keflex "Model 151-TR-1215"

SECTION 232113 - WATER SYSTEM SPECIALTIES

- Expansion Tanks and Accessories:

  - Bladder Type:  Steel, 125 psi wwp, ASME construction.  Heavy duty butyl rubber removable bladder.  Full acceptance vessel.

- Air Removal Assembly:  Bell & Gossett "Rolairtrol"/Taco/Armstrong.

- Air Eliminating Supply Fitting:  Bell & Gossett "Airtrol"/Taco/Armstrong.

- Flow Balancers:

  - 3 in. and Smaller:  Bell & Gossett "Circuit Setter"/Taco/Armstrong.

  - 4 in. and Larger:  Bell & Gossett "Circuit Sensor"/Taco/Armstrong.  Provide globe or plug style valve in conjunction with flow balancer for flow throttling.

  - Provide flow balancers for each piece of hydronic equipment including AHU coils, duct coils, fin radiation, unit ventilators and cabinet unit heaters.

- Triple Duty Valve:  Bell & Gossett "3D"/Taco/Armstrong.

- Backflow Preventer:  Watts No. 909.

SECTION 232123 - PUMPS

- In-line Centrifugal Pump:  Bell & Gossett "Series 60"/Taco/Armstrong.

- Base Mounted End Suction Pump:  Bell & Gossett "1510"/Taco/Armstrong.

- Provide suction diffuser, triple duty valve and concrete base pad for each base mounted pump.

- Provide inertia bases and spring type isolators when mechanical rooms are above occupied spaces.

SECTION 232213 - STEAM SPECIALTIES

- Radiation Valve:  Hoffman #184.

- Vacuum Breakers:  Hoffman #62.

- Thermostatic Trap (0 to 15 psi operating pressure):

  - Cast brass body, cap, union nut and nipple.  Duplex diaphragm or bellows type.  Stainless steel or brass removable seats and valves.

  - Provide on fin radiation, convectors and equipment under 10 MBH which does not handle outside air.

- Float and Thermostatic Trap (20 in. vacuum to 15 psi):

  - Cast iron body with drain tappings.  Stainless steel or brass float and renewable seat.  Thermostatic bypass.

  - Provide on AHU coils, unit ventilators and all equipment over 10 MBH or equipment which handles outside air.  Provide double traps on AHU coils which handle over 25% outside air.

- Strainers:

  - Cast iron or steel body.  Monel or stainless steel removable screen.  Blow-off and plug.

SECTION 233000 - SHEET METAL AND DUCTWORK ACCESSORIES

- Compliance with SMACNA and NFPA.

- Supply, Return, Relief and Exhaust:  Galvanized steel ASTM 525 construction.  All ductwork constructed to a minimum of SMACNA 2" pressure standard, higher ratings as required by job.

- Exposed painted:  Galvanealed.

- Pool and Shower Room Areas:  Aluminum construction.

- Outdoor Exposed Round Double Wall:  Galvanized steel with 4 mil PVS finish.

- Install filter media over supply grilles prior to starting fan.  Run fan for two days.  Remove filter media.  This work shall occur during a weekend or when the school is unoccupied.

SECTION 233313 - FIRE AND SMOKE DAMPERS

- Compliance with New York State Building Code and NFPA, and UL listed.

- Fire dampers:

  - Curtain type, galvanized steel.

  - 80% free area for velocities up to 1500 FPM.

  - 100% free area for velocities above 1500 FPM.

  - Ruskin “IBD2”, Nailor, NCA, Greenheck, Prefco.

- Smoke Dampers:

  - Multi-blade type, galvanized steel or aluminum.

  - Use airfoil type blade for duct velocities above 2000 FPM.

  - Ruskin “SD-50”, Prefco, Nailor, NCA, Greenheck.

SECTION 233400 - FANS

- All fans shall be AMCA rated.

- Ceiling Exhaust Fans:  Cook “Gemini”/Cook/Greenheck/Carnes/Acme/Penn.

- Rooftop Exhaust Fans:  Cook "Ace"/Penn/Carnes/Greenheck/Acme.

- Replace fan bearings with roller type when motors on original ventilation fans are replaced or fan RPM is increased:  Browning “22,5000 Series.”

SECTION 233616 - VARIABLE AIR VOLUME TERMINAL UNIT

- 22 gauge galvanized steel casing with 1/2" fiberglass internal insulation.

- Tight shutoff (2% leakage) internal damper.

- Averaging type multiple sampling point sensor, on cross grids.

- Titus "ESV-3000", Carnes, Price, Tuttle & Bailey, Trane.

SECTION 233713 - REGISTERS AND DIFFUSERS

- Exhaust and Return Grilles:  Titus "355-RL" or "23-RL"/Carnes/Price//Anemostat/Tuttle & Bailey.

- Heavy Duty Exhaust and Return Grilles:  Titus "33-RL"/Carnes/Price//Anemostat/Tuttle & Bailey.

- Supply Air Register:  Titus "272-FL"/Carnes/Price//Anemostat/Tuttle & Bailey.

- Supply Air Smooth Face Diffuser:  Titus "Omni"/Carnes/Price//Anemostat/Tuttle & Bailey.

- Supply Air Square Face Diffuser:  Titus "TMS"/Carnes/Price/Anemostat/Tuttle & Bailey.

- Cabinet Top Linear Bar Grilles - Diffuser "CT-PP-O"/Carnes/Price//Anemostat/Tuttle & Bailey.

  - Anodized finish only, painting is not acceptable.

SECTION 233726 - LOUVERS AND PENTHOUSES

- Louvers:

  - Extruded aluminum .125" minimum thickness.

  - Construction specialties "4130" and "6130", Arrow, Industrial Louvers, Vent Products, Greenheck.

- Louvered Penthouse:

  - Extruded heavy gauge aluminum.

  - Penn ventilator "Penn House", Carnes, Cook, Industrial Louvers, Vent Products.

- Non-Louvered Penthouse:

  - Heavy gauge aluminum construction.

  - Penn ventilator "Airette", Carnes, Cook.

4.	Provide drains in outside air intake plenums

SECTION 238316 – RADIANT HEATING PIPING

- Ratings shall be in accordance with approved IBR test methods.

- Fin tube radiation (high abuse areas, classrooms, corridors and toilet rooms):

  - 12 gauge partially perforated steel enclosure.  Sloped top.

  - .020" copper tube wall thickness with 020" aluminum fin thickness for hot water. Steel tube with .026" steel fin thickness for steam.

  - Silent cradle support for element and pipe.

  - Vulcan "PPS", Sterling, Shaw-Perkins.

- Fin Tube Radiation (Offices):

  - 16 gauge furniture steel, sloped top.

  - .020" copper tube wall thickness with 020" aluminum fin thickness for hot water. Steel tube with .026" steel fin thickness for steam.

  - Silent cradle support for element and pipe.

  - Vulcan "DS", Sterling, Trane, Rosemex

SECTION 235116- PREFABRICATED CHIMNEY (BOILER SERVICE)

- Designed to handle negative, neutral or positive internal pressures.

- Suitable for No. 2 oil and/or natural gas burners.

- Double wall construction with minimum 1" air space between walls, type 316 stainless steel for inner jacket (.035" thick for 6"-36" and .048" thick for 42"-48"),type 316 stainless steel for outer jacket exposed to weather, aluminized coated steel indoors (.025" thick for 6-24" and .034" thick for 28"-48").

- Metalbestos Model "PS", Van Packer, Stacks, Inc.

SECTION 235223 - CAST IRON BOILERS (STEAM AND HOT WATER)

- General:

  - Cast iron sectional type boiler.

  - Forced draft flame retention power burner, capable of burning No. 2 fuel oil and 1,000 BTU natural gas at available pressure.  Equal to Gordon-Piatt or Power Flame.

  - IBR tested and approved.

  - Fully modulating gas burner control.

  - Microprocessor based burner control system similar to "Honeywell 7800".

  - H.B. Smith Model "28A", Weil-McLain, Burnham as base bid.

  - H.B. Smith Model 3500/4500 "Header" type boilers as an add alternate.

- Hot water boilers for systems with central air handling systems and perimeter radiation.

  - Provide primary pumps to circulate water through boilers with secondary pumping loop to building systems.

  - Boiler primary loop scheduled for 140oF to 200oF.

  - Building secondary loop scheduled as required, subject to 40oF temperature difference across the boilers.

- Steam boilers for systems with unit ventilators.

- Multiple modular hot water boilers for “tight” Boiler Rooms:  RBI – Futura II.

- .Fireye burner/Logix ZB11OUV/1R with modbus on boilers up to 125 HP.

- Fireye Nexus with modbus on boilers 150 HP and larger.

- Steam boilers to have a water softener on makeup water.

- Steam boiler chemical treatment system to include:  conductivity controller, auto blow-down, pulse meter on makeup water, 5 gallon bulk storage for oxygen scavenger and chemical treatment, and interface to DDC system.

SECTION 236000 - CHILLERS

- Chiller installation shall meet the requirements of ASHRAE Standard 15-1994.

- Air cooled rooftop chillers shall have a service platform for easy access to control panel.

- Centrifugal chillers hall have re-seatable Rupture disks.

- Acceptable Make:  Trane.

SECTION 237313 - AIR HANDLING UNITS

- Double wall casing construction with 1-1/2 Lb./Ft.3 density insulation.

- Two inch pleated type, 30% efficient, filters minimum.  Units over 10,000 cfm shall have 65% bag or box final filters.  One (1) start-up set plus one (1) spare set.

- Outside air dampers shall be low-leak type.

- Trane "Modular Climate Changer", Carrier, York, McQuay.

SECTION 238223 - UNIT VENTILATORS

- 16 gauge steel cabinet.

- Full adapter back outside air intake, provide watertight stainless steel baffle in plenum pitched to outside air intake.

- Steam:  Face and bypass damper control, and control valve for applications where mixed air temperature is below 40oF.  All other applications to have valve control only.

- Hot Water:   Control valve.

- 1" thick 20% efficient pleated filters accessible through return air grille.  One (1) start-up set plus one (1) spare set.

- Unit vent DDC control board shall be located in a separate 12 in. accessory compartment or in a lockable cabinet above the ceiling.  Control board location shall be marked on ceiling tile and on asbuilt control drawings.

- AAF - Herman Nelson "AV" and "AH", Trane

SECTION 238229 – RADIATORS

1.	Provide covers for all radiators to prevent student injury.

SECTION 238223 - UNIT HEATERS AND CABINET UNIT HEATERS

- Serpentine coil, copper tube, aluminum fins.

- Cabinet unit heater - 16 gauge steel.

- Trane "UHS" and "FC", Sterling, Modine, Airtherm.

SECTION 238216 - COILS

- Hot water and chilled water shall be drainable type, designed for 125 psi.

- Steam shall be double tube non-freeze type for equipment handling outside air and for unit ventilators.

- Aluminum fins shall be a minimum of .0075" thick.

- Brazed return "U" bends, bent tubes not acceptable.

- Minimum .035" thick copper tubes and "U" bends.

- Provide stainless steel drip pan under chilled water coils.

- Coils shall be ARI rated.

SECTION 238419 - PACKAGED POOL DEHUMIDIFICATION AND HEAT RECOVERY UNIT

- Pools shall be conditioned using packaged pool dehumidification units with air to air heat exchange capability.  Design shall incorporate diffusers for direct air movement over glass surfaces and minimize air movement over pool surface.

- Provide variable speed supply and exhaust fans.  Filters shall be minimum 2" thick, 30% efficient pleated filters.

- Unit shall be capable of providing outside air equal to .5 cfm/sq. ft. of pool and deck area.

- Pool environment shall be designed for pool air at 80-85oF (55 to 60% RH) and pool water at 80-85oF.  Exact conditions to be verified with building occupants.

- Air to air heat exchange shall be accomplished with a heat pipe.

- Unit housing and fans shall be aluminum.

- Provide auxiliary hot water/steam coil in unit.

- Unit control panel shall be interfaced with building DDC system for alarms, adjusting setpoints and reading/monitoring sensors.

- Rooftop units shall be avoided.

- Acceptable Make:  Efficient Air Systems, Inc.